**Pumps – Pump Station #4**

The Harrison County Development Commission (HCDC) will receive the sealed bids for *replacing pumps for pump station No. 4*, located within the Bernard Bayou Industrial District in Harrison County, Mississippi. Said bids will be accepted until **Wednesday, August 28th, 2019**, at **10 a.m. central standard time** at the HCDC offices, located at **12281 Intraplex Parkway Gulfport, MS 39503**. In accordance with the law set forth by the State Auditor of Mississippi, the bids will be opened and publicly read aloud the following day (**Thursday, August 29th, 2019**). Contract requirements and specifications will be available for the inspection at the HCDC offices, you may also call **228-896-5020** or email *bids@mscoast.org*. For jobs awarded, it is the vendors responsibility to ensure HCDC receives certificates of liability/workers’ comp prior to each expiration year. The Commission reserves the right to reject any and all bids. Bids must be considered valid for a period of 90 days.

**Specifications**:

1. Pumps Must be **6 in. discharge**, **40 horsepower**, including **6 in. x 6 in. discharge base elbows**.
	1. **Pumps shall operate on 3 phase, 60HZ, 480volt power.**
2. Pumps shall be non-clogging chopper variety delivering solids size reduction.
3. Pumps shall have **heat treated 440c stainless cutter blades** capable of handling **solids larger than 3 in**.
4. Pumps must employ **quick disconnect cords**; a minimum of 50 ft. in length.
5. Blades must be field replaceable.
6. Pumps shall have stainless lifting bails, VRD ready motors with 1.2 service, factor, class H magnet wire, tapered key shaft. Stainless hardware, heat treated open center design blades.
7. Liquid cooled motor with high capacity (**50,000 hour bearing life at 2 ft /sec flow**).
8. Pumps shall be **coated with Axalta Epoxy**.
9. **Slotted Discharge** that adapts to ANSI and ISO flanges.
10. Payment for said pumps shall be in accordance with the Commissions standard billing procedures (**approximately 30 days**).
11. Product shall be delivered **F.O.B. Gulfport, MS 39503**.
12. Pumps shall be warrantied for both parts and labor for the period of **no less than 5 years**.
13. Pump packages shall be complete with cords, seal materials, break away fittings, adapters, electric panels, level controls and stainless-steel pump slide rails including mounting hardware.
14. **Certificate of Liability** and **Workers’ Comp** must be included with each submitted bid.
	1. **These certificates must be presented to HCDC each contractual year, prior to expiration.**
	2. **These Certificates may not be necessary for sale only bids**
15. MPC Number – **Material Purchase Certificate** and Contractor Qualifications must be provided to HCDC.