hazlehurst city school district

2015 RFP

Project Lighting System

RFP#2015-1

Project Coordinator:  Mark Douglas, Facilities Director

119 Robert McDaniel Drive

Hazlehurst, MS  39083

(601) 894-1152

mdouglas@hazlehurst.k12.ms.us

1.	GENERAL PROJECT DESCRIPTION

This project is intended to replace existing athletic light poles and fixtures and replace them with a system as outlined herein.  Throughout construction, installation and testing of the new system, the existing lighting system shall remain operational and the football field shall remain open for use.

2.	PROJECT REQUIREMENTS, DESIGN AND EXECUTION

PROJECT LIGHTING SYSTEM REQUIREMENTS

Summary

- Work covered by this section of the specifications shall conform to the contract documents, engineering plans as well as state and local codes.

- The purpose of these specifications is to define the performance and design standards for the Hazlehurst football stadium. The manufacturer / contractor shall supply lighting equipment to meet or exceed the standards set forth in these specifications.

- The sports lighting will be for the following fields:

  - High School Football Field

- The primary goals of this sports lighting project are, in order of importance:

  - Guaranteed Light Levels

Selection of appropriate light levels impact the safety of the players and the enjoyment of spectators.  Therefore light levels are guaranteed for a period of 25 years.

  - Control and Monitoring

To allow for optimized use of labor resources and avoid unneeded operation of the facility, customer requires a remote on/off control system for the lighting system.  Fields should be proactively monitored to detect fixture outages over a 25 year life-cycle.

  - Life-cycle Cost

In order to reduce the operating budget, the preferred lighting system shall be energy efficient and cost-effective to operate.

Lighting Performance

# Performance Requirements

# Playing surfaces shall be lit to an average constant light level and uniformity as specified in the chart below. Light levels shall be held constant for 25 years. Lighting calculations shall be developed and field measurements taken on the grid spacing with the minimum number of grid points specified below. Average illumination level shall be measured in accordance with the IESNA LM-5-04. Light levels shall be guaranteed from the first 100 hours of operation for the maximum warranty period.

| Area of Lighting | Average Constant Light Levels | Maximum to Minimum Uniformity Ratio | Grid Points | Grid Spacing |
| --- | --- | --- | --- | --- |
| Football Field | 50 footcandles | 2.0:1.0 infield | 72 | 30’ x 30’ |

- Lumen Maintenance Control Strategy

A constant light system shall use automatic power adjustments to achieve a lumen maintenance control strategy as described in the IESNA Lighting Handbook 10th Edition, Lighting Controls Section, page 16-8:  "Lumen maintenance involves adjusting lamp output over time to maintain constant light output as lamps age, and dirt accumulation reduces luminaire output.  With lumen maintenance control, either lamps are dimmed when new, or the lamp's current is increased as the system ages."

- Independent Test Report

Manufacturers bidding any form of a constant light system must provide an independent test report certifying the system meets the lumen maintenance control strategy above and verifying the field performance of the system for the duration of the useful life of the lamp based on lamp replacement hours.  Report shall be signed by a licensed professional engineer with outdoor lighting experience.  If report is not provided at least 10 days prior to bid opening, the manufacturer shall provide the initial and maintained designs called for in this specification under Alternate Manufacturers, section 1.7.

- Project References

Manufacturers bidding any form of a constant light system must provide a minimum of two (2) project references that have been completed within the last three (3) calendar years utilizing specifications as stated in this RFP. Manufacturer will include project name, project city, and if requested, contact name and contact phone number for each reference.

- Mounting Heights

To ensure proper aiming angles for reduced glare and to provide better playability, the pole mounting heights from the playing field surface shall be 80’.

Life Cycle Costs

- Energy Consumption

The average kW consumption for the field lighting system shall be 80kW or less.

- Complete Lamp Replacement

Manufacturer shall include all group lamp replacements required to provide 25 years of operation based upon 200 usage hours per year.

- Preventative and Spot Maintenance

Manufacturer shall provide all preventative and spot maintenance, including parts and labor for 25 years from the date of equipment shipment. Individual lamp outages shall be repaired when the usage of any field is materially impacted. District agrees to check fuses in the event of a luminaire outage.

- Remote Monitoring System

All bidders must provide monitoring lighting performance and notify manufacturer if individual luminaire outage is detected so that appropriate maintenance can be scheduled.  The manufacturer shall notify the district of outages within 24 hours, or the next business day.  The controller shall determine switch position (Manual or Auto) and contactor status (open or closed).

- Remote Lighting Control System

System shall allow district and users with a security code to schedule on/off system operation via a web site, phone, fax or email up to no less than six months in advance.  Manufacturer shall provide and maintain a two-way TCP/IP communication link.  Trained staff shall be available 24/7 to provide scheduling support and assist with reporting needs.

The district may assign various security levels to schedulers by function and/or fields.  This function must be flexible to allow a range of privileges such as full scheduling capabilities for all fields, to only having permission to execute “early off” commands by phone.

Controller shall accept and store seven day schedules, be protected against memory loss during power outages, and shall reboot once power is regained and execute any commands that would have occurred during outage.

- Management Tools

Manufacturer shall provide a web-based database of actual field lighting usage and provide reports by facility and user group.

  - Hours of Usage: Manufacturer shall provide a means of tracking actual hours of usage for the field lighting system that is readily accessible to the district.

  - Cumulative Hours: shall be tracked to show the total hours used by the facility

  - Current Lamp Hours:  shall be tracked separately to reflect the amount of hours on the current set of lamps being used, so re-lamping can be scheduled accurately

- Communication Costs

Manufacturer shall include communication costs for operating the controls and monitoring system for a period of 25 years.

- 25 -Year Life-cycle Cost

Manufacturer shall submit 25-year life-cycle cost calculations as follows.  Equipment price and total life-cycle cost shall be entered separately on bid form (See APPENDIX A) for evaluation purposes.  Life-cycle costs shall not be the sole determining factor in awarding a bid.

| a. | Luminaire Energy Consumption # luminaires x __kW demand per luminaire x .10 kWh rate x 500 annual usage hours x 25 years |  |  |
| --- | --- | --- | --- |
| b. | Demand charges, if applicable | + |  |
| c. | Cost for spot re-lamping and maintenance over 25 years Assume 7.5 repairs at $500 each if not included with the bid | + |  |
| d. | Cost to re-lamp all luminaires during 25 years 100 annual usage hours x 25 years / 2100 hours x $125 lamp & labor x # fixtures if not included with the bid | + |  |
| e. | Extra energy used without base bid automated control system $ Energy consumption in item a. x 25% if control system not included with the bid | + |  |
|  | TOTAL 25 -Year Life-cycle Operating Cost | = |  |

Warranty and Guarantee

  - 25-Year Warranty

Each manufacturer shall supply a signed warranty covering the entire system for twenty-five (25) years OR for the maximum hours of coverage based on the estimated annual usage, whichever occurs first.  Warranty shall guarantee light levels; lamp replacements; system energy consumption; monitoring, maintenance and control services, spill light control, and structural integrity.  Manufacturer shall maintain specifically-funded financial reserves to assure fulfillment of the warranty for the full term.  Warranty may exclude fuses, storm damage, vandalism, abuse and unauthorized repairs or alterations.  Group lamp replacements for constant light systems must occur in accordance with the independent test report provided by the manufacturer; alternate systems must re-lamp every 2,100 hours.

Delivery Timing

- Equipment On-Site

The equipment must be on-site within four (4) weeks or less from date of approved purchase order and Notice to Proceed.

Pre-Bid Submittal Requirements

    - Product Approval

Musco Light Structure Green is the approved product.  All other manufacturers are required to  provide a complete submittal package via email to the Project Coordinator for approval as outlined in Submittal Information at the end of this section at least 5-days prior closing date  Special manufacturing to meet the standards of this specification may be required.  An addendum will be issued prior to bid listing any other approved lighting manufacturers and designs.

    - Design Approval

The District will review pre-bid shop drawings from the manufacturer for any alternate product to ensure compliance to the specification.  If the design meets the design requirements of the specifications, a letter will be issued via email to the manufacturer indicating approval for the specific design submitted.

Alternate System Requirements

- Compliance to Specifications

Acceptance of a bid alternate does not negate the contractor and lighting manufacturer’s responsibility to comply fully with the requirements of these specifications. Any exceptions to the specifications must be clearly stated in the prior approval submittal documents.

- Light Level Requirements

Manufacturer shall provide computer models guaranteeing light levels on the field over 25 years.  If a constant light level cannot be provided, the specified maximum Recoverable Light Loss Factor and maintenance/group re-lamping schedule shall be provided in accordance with recommendations in the Pennsylvania State University report “Empirical Light Loss Factors for Sports Lighting”, presented at the 2009 IESNA Annual Conference.

| Lamp Replacement Interval (hours) | Recoverable Light Loss Factor (RLLF) |
| --- | --- |
| 2100 | 0.69 |

For alternate systems, scans for both initial and maintained light levels are required.

| Area of Lighting | Average Initial Light Levels | Average Target/Maintained Light Levels | Maximum to Minimum Uniformity Ratio | Grid Points | Grid Spacing |
| --- | --- | --- | --- | --- | --- |
| Football | 72 footcandles | 50 footcandles | 2.0:1.0 infield | 72 | 72 |

- Revised Electrical Distribution

Manufacturer shall provide revised electrical distribution plans to include changes to service entrance, panel, and wire sizing.

PRODUCT

Lighting System Construction

- System Description:  Lighting system shall consist of the following:

  - Galvanized steel poles and cross-arm assembly

  - Pre-stressed concrete base embedded in concrete backfill allowed to cure for 12-24 hours before pole stress is applied.  Alternate may be an anchor bolt foundation designed such that the steel pole and any exposed steel portion of the foundation is located a minimum of 18 inches above final grade.  The concrete for anchor bolt foundations shall be allowed to cure for a minimum of 28 days before the pole stress is applied. Concrete or direct buried steel poles or concrete encased steel poles shall not be allowed.

  - All luminaires shall be constructed with a die-cast aluminum housing or external hail shroud to protect the luminaire reflector system.

  - Manufacturer will remote all ballasts and supporting electrical equipment in aluminum enclosures mounted approximately 10’ above grade.  The enclosures shall include ballast, capacitor and touch-safe fusing to indicate when a fuse is to be replaced for each luminaire.

  - Wire harness complete with an abrasion protection sleeve, strain relief and plug-in connections for fast, trouble-free installation.

  - Controls and Monitoring Cabinet to provide on-off control and monitoring of the lighting system, constructed of NEMA Type 4 aluminum.  Communication method shall be provided by manufacturer.  Cabinet shall contain custom configured contactor modules for 30, 60, and 100 amps, labeled to match field diagrams and electrical design.  Manual Off-On-Auto selector switches shall be provided.

  - Manufacturing Requirements

All components shall be designed and manufactured as a system. All luminaires, wire harnesses, ballast and other enclosures shall be factory assembled, aimed, wired and tested.

  - Durability

All exposed components shall be constructed of corrosion resistant material and/or coated to help prevent corrosion.  All exposed carbon steel shall be hot dip galvanized per ASTM A123.  All exposed aluminum shall be powder coated with high performance polyester or anodized.  All exterior reflective inserts shall be anodized, coated, and protected from direct environmental exposure to prevent reflective degradation or corrosion.  All exposed hardware and fasteners shall be stainless steel of 18-8 grade or better, passivated and coated with aluminum-based thermosetting epoxy resin for protection against corrosion and stress corrosion cracking.  Structural fasteners may be carbon steel and galvanized meeting ASTM A153 and ISO/EN 1461 (for hot dipped galvanizing), or ASTM B695 (for mechanical galvanizing).  All wiring shall be enclosed within the cross-arms, pole, or electrical components enclosure.

  - Lightning Protection

Manufacturer shall provide integrated lightning grounding via concrete encased electrode grounding system as defined by NFPA 780 and be UL Listed per UL 96 and UL 96A.

If grounding is not integrated into the structure, the Manufacturer shall supply grounding electrodes, copper down conductors and exothermic weld kits.  Electrodes and conductors shall be sized as required by NFPA 780.  The grounding electrode shall be not less than 5/8 inch diameter and 8 feet long, with a minimum of 10 feet embedment.  Grounding electrode shall be connected to the structure by a grounding electrode conductor with a minimum size of 2 AWG for poles with 75 feet mounting height or less, and 2/0 AWG for poles with more than 75 feet mounting height.

  - Safety

All system components shall be UL Listed for the appropriate application.

  - Electric Power Requirements for the Sports Lighting Equipment:

  - Electric power: 208 Volt, Three (3) Phase

  - Maximum total voltage drop: Voltage drop to the disconnect switch located on the poles shall not exceed three (3) percent of the rated voltage.

Structural Parameters

- Support Structure Wind Load Strength

Poles and other support structures, brackets, arms, bases, anchorages and foundations shall be determined based on the 2009 IBC Building Code, wind speed of 100 MPH, exposure category C and an importance factor of 1.0. Luminaire, visor, and cross-arm shall withstand 150 mph winds and maintain luminaire aiming alignment.

- Structural Design

The stress analysis and safety factor of the poles shall conform to AASHTO 2009 (LTS-5) Standard Specifications for Structural Supports for Highway Signs, Luminaires and Traffic Signals.

- Soil Conditions

The design criteria for these specifications are based on soil design parameters as outlined in the geotechnical report. If a geotechnical report is not provided by the district, the foundation design shall be based on soils that meet or exceed those of a Class 5 material as defined by 2009 IBC.

It shall be the contractor’s responsibility to notify the district if soil conditions exist other than those on which the foundation design is based, or if the soil cannot be readily excavated. Contractor may issue a change order request / estimate for the district’s approval / payment for additional costs associated with:

- Providing engineered foundation embedment design by a registered engineer in the State of Mississippi.

- Additional materials required to achieve alternate foundation.

- Excavation and removal of materials other than normal soils, such as rock, caliche, etc.

- Foundation Drawings

Project specific foundation drawings stamped by a registered engineer in the state where the project is located are required.  The foundation drawings must list the moment, shear (horizontal) force, and axial (vertical) force at ground level for each pole.  These drawings must be submitted at time of bid to allow for accurate pricing.

Electrical System Requirements

- Contractor Responsibility

The installing contractor shall be responsible for providing the equipment and installation of a complete and operational system commencing from the secondary side of the service transformer and terminating at the safety disconnect within the electrical enclosure, 10’ above grade, on each lighting pole.  The electrical contractor shall coordinate the transformer and switchgear locations, as well as identifying the voltage and phase of the service, with the local power company and the District’s Project Coordinator before any equipment is installed.

- Electric Power Requirements for the Sports Lighting Equipment: 208 Volt, Three (3) Phase

- Maximum Total Voltage Drop

Voltage drop to the disconnect switch located on the poles shall not exceed three (3) percent of the rated voltage.

- System Design

- The electrical system equipment shall consist of:

  - Conductors in conduit from the main service transformer to the service entrance panel board.

  - The service entrance 400 Amp 3 phase 42 circuit main circuit breaker panel board with appropriate individual circuit over-current protection.  The panel board shall meet local and National Electrical Code (NEC) requirements for the size of the service, AIC rating, and the type of the environment to which it will be exposed.  All feeder breakers shall be bolt on type.

  - Conductors in conduit for the feeder circuit from the service entrance panel board (or from the contactor panel if applicable) to the safety disconnect mounted in the electrical enclosure on each lighting pole 10’ above grade.

  - Demolition of all existing wood poles inside walking track, one wood pole on the Southwest corner of the field just outside of the walking track, and one wood pole on the East of the field just outside of the walking track with exception to the existing DIP pole. Existing DIP pole to remain. The existing panel board and all existing equipment rack materials to be demolished. All items on demolished poles are to be turned over to the district for re-use or disposal. All unused existing overhead wiring on demolished poles is to be turned over to the district for re-use or disposal.

  - One new 20’ power pole shall be installed between the visitor bathroom and concession building. Relocate existing overhead from field lighting standard feeding existing area light in Northwest Corner of the property to new power pole. Relocate existing overhead from field lighting standard feeding visitor concession building to new power pole. New power pole shall be fitted with a new 100 Amp 3 phase 12 circuit main lug only outdoor panel board. The load at this panel board shall be calculated at 30 Amps 3 phase 208 volts and shall feed underground from new service entrance panel board with minimum #2 conductors. Appropriate individual circuit over-current protection shall be installed in this panel to re-feed existing relocated overhead conductors to concession building and area lighting.

  - The existing power pole located next to the Home concession building shall be straightened to plumb. A new 100 Amp 3 phase 12 circuit main lug only outdoor panel board shall be mounted to the pole. The load at this panel board shall be calculated at 50 Amps 3 phase 208 volts and shall feed underground from new service entrance panel board with minimum #1/0 copper conductors. Appropriate individual circuit over-current protection shall be installed in this panel to re-feed existing overhead conductors to press box, concession building, bathroom building, and ticket booths.

  - Disconnect existing overhead feeder from existing field lighting standards to existing power pole located by and feeding bathroom at West end of field by scoreboard. Re-feed this pole underground from new service entrance panel board with a calculated load of 30 Amps 3 phase 208 volts and minimum #1 conductors.

  - A new power pedestal equal to Milbank model # U5200-XL-322 shall be mounted at approximately the 50 yard line east and west and next to the walking track. A 12”X12”X4” concrete pad shall be constructed around the power pedestal. The load at this power pedestal shall be calculated at 50A 1 phase 208 volts and shall feed underground from new service entrance panel board with minimum #2 copper conductors.

  - Grounding conductors and grounding methods for the following:

        - The main service entrance panel board. (per NEC or local codes)

        - The lighting contactor enclosure. (per NEC or local codes)

        - Each electrical component enclosure mounted on the lighting poles.  (Equipment Grounding System) (per NEC or local codes)

        - Lightning Protection for individual poles as follows (per NFPA 780):

            - A 5/8 inch x 8 foot copper-clad grounding electrode buried vertically in undisturbed earth.  The bottom tip of the grounding electrode should reach a minimum of 10 feet below grade.

            - A copper grounding electrode conductor shall be connected to the top of the grounding electrode and extend and connect to the grounding lug located inside the handhole of the pole approximately 10 feet above grade.  The size of this conductor shall be 2 AWG if the pole is 75 feet in height or less, and 2/0 AWG if the pole is greater than 75 feet.

- Underground wiring shall be all copper wire and shall be installed in PVC Schedule 40 conduit for below grade applications and shall be buried to a depth meeting the NEC and local electrical codes.  Acceptable copper wire types need to comply with any local requirements, but will be labeled either THHN or THWN.  If above ground conduit must be used, it shall be rigid galvanized steel.  Conduit elbows located at the electrical panel shall be rigid galvanized steel.

- Trenching or Directional Boring

      - The installing contractor shall be responsible for locating all underground utilities including, but not limited to: natural gas, electric, water, sewer, cable TV, and telephone.

      - The district shall be responsible for locating and staking any underground facilities that are not utility related.  The district accepts responsibility for damage to such facilities that are not properly located or staked.

      - Trenching depth and width shall be adequate to install appropriately sized conduit and to meet local and National Electrical Codes.

      - Trenches shall be back-filled with excavated soil and compacted to approximately the same density of the surrounding soil to minimize settlement.

      - No trench line or feeder circuit shall cross the playing area of The Hazlehurst High School football field.

- Design Standards

- All circuits shall be designed so that the voltage at the safety disconnect in the electrical enclosure near the base of each pole is within 3% of nominal.

- All work shall meet local and National Electrical Codes.  It shall be the installing contractors’ responsibility to correct any work deemed unacceptable by local electrical inspectors. The installing contractor shall provide an electrical distribution plan stamped by a P.E in the state of Mississippi.

- All electrical components shall be UL Listed for the appropriate application.

- Each pole shall be on a dedicated circuit.  If common poles are used, or a pole is to have fixtures on separate circuits, multiple dedicated circuits shall be run to that pole.  Consult lighting equipment specifications and lighting manufacturer for special circuitry information.

- Submittal Information

The successful contractor shall provide an electrical plan/schematic, detailing all of the equipment described above, to the district for approval prior to commencing work.  This electrical plan/schematic shall bear the stamp of an Electrical Engineer with P.E. status within the State of Mississippi.

Contractor's Duties

All work performed under this contract shall be performed in accordance with all provisions of these specifications and drawings.  Any deviations from the specifications or plans must be approved in writing by the district.

- Initial Site Inspection

The Contractor shall be presumed to have made a reasonable inspection of the premises prior to the time of bidding and shall be held responsible for all information available through such inspection.  The contractor shall immediately upon discovery, bring to the attention of the district any conflicts that may occur among the various provisions of the specifications and plans.  The district shall resolve such conflicts and shall be responsible for any costs reasonably incurred by the contractor due to such conflict.  Failure of the contractor to bring conflicts or exceptions to the attention of the district shall allow the district to require any change deemed necessary before acceptance by the district.

- Insurance Requirements

The Contractor shall not commence work under this Contract until they have obtained all insurance required under this paragraph and such insurance has been approved by the District, nor shall the Contractor allow any sub-contractor to commence work on his subcontract until all similar insurance required of the sub-contractor has been so obtained and approved.  The Hazlehurst City School District shall be named as additionally insured by all policies required under this section.  Satisfactory proof of the required insurance shall be furnished to the District.

| COVERAGES | LIMITS OF LIABILITY |
| --- | --- |
| Workmen's Compensation | Statutory |
| Employer's Liability | $500,000 |
| Bodily Injury Liability Except Automobile | $500,000 each occurrence $500,000 aggregate |
| Property Damage Liability Except Automobile | $300,000 each occurrence $300,000 aggregate |
| Automobile Bodily Injury Liability | $500,000 each person |
| Automobile Property Damage Liability | $500,000 each occurrence |

The Contractor shall provide the District, at the time contracts are returned for execution, one copy of, certificates and policies listed above.  A guarantee that a ten (10) day notice to the District prior to cancellation of, or change in any such insurance, shall be in force on each policy and certificate of insurance.

- Bonding

The successful contractor shall furnish a performance bond in an amount equal to one hundred percent (100%) of the contract as security for the faithful performance of this contract, and a labor and material payment bond in an amount of one hundred percent (100%), or in the penal sum not greater than that prescribed by state, territory, or local law, as security for the payment of all persons performing labor on the project under this contract and furnishing materials in connection with this contract.  The bonds shall be written by a surety licensed to do business in the locale in which the work is being performed and shall be satisfactory to the district.

The successful contractor shall, upon completion of the project, protect the district against defective materials or faulty workmanship for a period of two (2) years.  The contractor, at the district’s request, shall furnish a maintenance bond for the above outlined maintenance term.  This bond shall be in an amount not to exceed one hundred percent (100%) of the contract price.

- Codes, Permits and Licenses

All work shall comply with the applicable rules of the National Electrical Code, the National Electrical Safety Code, the National Fire Codes, (published by the National Fire Protection Association), state and local codes and ordinances, and the terms and conditions of the services of the electrical utility, as well as any other authorities that may have lawful jurisdiction pertaining to the work specified.  None of the terms or provisions of this specification shall be construed as waiving any of the rules, regulations or requirements of these authorities.  The contractor shall procure all necessary permits or licenses to carry out the work, and shall pay the lawful fee therefore, as well as for any inspection fee or the cost of a certificate of approval.

In any instance where these specifications call for materials for construction of a better quality or larger size than required by the codes, the provisions of these specifications shall take precedence.  The codes shall govern in the case of direct conflict between the codes and the plans and the specifications.

Materials

- Approved Materials

All materials supplied by the contractor under the provisions of these specifications and plans shall be new materials of the kind and character called for by the specifications.  Defective equipment or material damaged in the course of installation or tests shall be replaced or repaired in a manner satisfactory to the district.  All materials and equipment to be furnished under these specifications shall be the standard product of a manufacturer regularly engaged in the production of such material and shall be the manufacturer’s current standard design.

- Alternate Materials

The materials specified have been determined to have characteristics appropriate for the purposes of this project.  Alternate materials will only be considered as a substitute bid on a separate substitution sheet.  No bid will be approved which proposes to use a non-approved substitute.  Substitutions will not be considered in determining the lowest responsive bid.  The district reserves the right to reject any or all bids received.

Site Access

- Contractor Access

For the performance of the contract, the contractor will be permitted to occupy such portions of the site as shown on the plans, or as permitted by the district or his Project Coordinator.  A reasonable amount of tools, materials or equipment for construction purposes may be stored in such place, but not more than is necessary to avoid delays in construction.  Excavated and waste materials shall be piled or stocked in such a way as to not interfere with spaces that may be designated to be left free and unobstructed, not to inconvenience other contractors or the district.

- District’s Access:

The district’s Project Coordinator shall at all times have access to the work site.  The contractor shall keep the district advised of the progress of the project and shall provide opportunity for the district’s Project Coordinator to inspect each phase of the project.  The contractor shall provide proper and safe facilities for such access and for inspection.

Replacement of Damaged Property

The contractor shall replace all property damaged including fences, trees, plants, grass, walks, drives, building surfaces, etc.

Installation

- Manufacturer’s Instructions

Written instructions for the installation of the sports lighting equipment shall be provided by the manufacturer.  The contractor shall review the instructions prior to beginning installation and review any areas of concern with the manufacturer.

- Installation of Equipment

Contractor shall install lighting equipment per manufacturer’s stated requirements to ensure lighting performance is achieved.

- Manufacturer Project Coordinator

A qualified Project Coordinator from the sports lighting manufacturer shall be available to provide installation guidance if required by the contractor.

- Handling of Equipment

The lighting equipment shall be handled in an appropriate manner to ensure safe installation and prevent damage to the equipment.  Repair or replacement of damaged component shall be the responsibility of the installing contractor.

- Rigging

Use the appropriate rated web fabric slings to lift components into position.  Chains or cables shall not be allowed due to potential failure and damage to components.

- Completion Time

All construction, after approved purchase order and Notice to Proceed, is to be completed within ninety (90) calendar days.  If construction is not completed within the specified period, and the delay is due to the fault of the Contractor, the District may charge the contractor liquidated damages in the amount of $500 per day.  The contractor will be required to commence work within ten (10) calendar days after the district issues an approved purchase order and written Notice to Proceed, shall be present at the job site during normal working hours and shall proceed to completion with due diligence.

- Existing Lighting System

  - To Remain Operational

The existing lighting system in place at the field is to remain in an operational condition throughout the duration of the installation and testing of the new lighting system.  Field may be in use for play throughout the installation and testing of the new lighting system.  Contractor shall advise the District if any portion of the project shall result in a need to temporarily close the field.

  - Removal

Upon completion of the work and before acceptance and final payment is made, the Contractor shall disconnect and remove all existing field lighting, related wiring and support poles from the site.

- Clean-up

Upon completion of the work and before acceptance and final payment is made, the contractor shall clean and remove from the site of the work, surplus and discarded materials, temporary structures and debris of every kind.  The contractor shall leave the site of work in a neat and orderly condition equal to that which originally existed.  Surplus and waste materials removed from the site of the work shall be disposed of at locations satisfactory to the district.

Field Quality Control

- Illumination Measurements

Upon substantial completion of the project and in the presence of the Contractor, Project Engineer, District's Project Coordinator, and Manufacturer's Project Coordinator, illumination measurements shall be taken and verified.  The illumination measurements shall be conducted in accordance with IESNA RP-6-01, Appendix

- Correcting Non-Conformance

If, in the opinion of the District or Project Coordinator, the actual performance levels are not in conformance with the requirements of the lighting equipment performance specifications and submitted information, the Contractor shall be liable to any or all of the following if installation of the lighting equipment does not conform to manufacturer’s stated requirements:

  - At contractor’s expense provide and install any necessary additional fixtures to meet the minimum lighting standards. The contractor shall also either replace the existing poles to meet the new wind load (EPA) requirements or verify by certification by a licensed structural engineer that the existing poles will withstand the additional wind load.

  - Contractor shall minimize the District's additional long term fixture maintenance and energy consumption costs created by the additional fixtures by reimbursing the District the amount of $1,000.00 (one thousand dollars) for each additional fixture required.

  - Contractor shall remove the entire unacceptable lighting system and install a new lighting system to meet the specifications.

3.	RESPONSE INSTRUCTIONS

The submitted proposal must follow the rules and format established within this RFP.  Adherence to these rules will ensure a fair and objective analysis of all proposals.  Failure to complete any portion of this request may result, at the District’s sole discretion, in the rejection of a proposal.

4.	COMMUNICATION WITH THE DISTRICT

To ensure a fair and objective evaluation of all proposals, vendors are required to submit all inquiries to the Project Coordinator identified on the cover of this document.

The District will host a Pre-Bid Meeting on March 19, 2015 at 9:00 am at The Hazlehurst City School District’s Administrative Office located at 119 Robert McDaniel Drive, Hazlehurst, MS  39083.  The purpose of this meeting is to allow vendors to review the scope of the project with staff and to ask questions regarding the project while ensuring that all vendors receive an equal opportunity to receive information regarding the project.  All bidders must attend the Pre-Bid Meeting.

5.	ASSESS BID DOCUMENTS

Before submitting a proposal, vendors shall examine the specifications in order to understand all existing conditions and limitations.  The vendor shall indicate in the proposal the total sum to cover the cost of all items included in this RFP.

6.	COSTS OF BID PREPARATION AND SUBMISSION

Each vendor shall be responsible for all costs incurred in order to prepare and submit their response to this Call for Bids.

7.	PROPOSAL REVIEW

All bids will be opened and read aloud at the time and place indicated in the Selection Schedule of this RFP.  All documents submitted as part of the vendor’s bid will be deemed confidential during the evaluation process.  Vendor proposals will not be available for review by anyone other than the District’s evaluation committee.  There shall be no disclosure of any vendor’s information to a competing vendor prior to the evaluation team making a recommendation.  All applicable information will be subject to public disclosure in accordance with the Freedom of Information Act, at award of contract, cancellation of the project, or within 180 days, whichever shall occur first.

8.	PROPOSAL

Each proposal will be submitted on the Bid Submission Form provided herein and be submitted in a sealed envelope bearing the project number, project title and the name of the vendor.  Proposals shall be submitted to the below address:

119 Robert McDaniel Drive

Hazlehurst, MS  39083

Proposals must be received no later than 10:00 AM on April 9, 2015.

Proposals received by the closing date and time will be opened and evaluated by the District’s evaluation committee.  Proposals not received by the closing date and time will remain unopened and will not be considered.  Incomplete proposals may, at the District’s sole discretion, be disqualified from consideration.

Delivery of Proposals:  Responses to this RFP must be delivered by the date/time specified and to the place stipulated on the cover of this document.  It is the sole responsibility of the vendor to see that their submission is received in the proper time.

The District reserves the right to amend or clarify the specifications at any time prior to the closing for receipt of proposals.  It is the sole responsibility of the vendor to periodically visit The Hazlehurst City School District’s website, www.hazlehurst.k12.ms.us to check for RFP updates, as well as, any and all inquiries, questions, and answers submitted from vendors.

9.	RIGHT OF REFUSAL

The District reserves the right to reject any or all bids in their entirety and also reserves the right to award the contract in any manner deemed in the best interest of the District.

10.  	EVALUATIONS

The primary criteria for vendor evaluation and consideration are:

| Total Project Cost | 30% |
| --- | --- |
| Completeness and thoroughness of proposal | 5% |
| Demonstrated ability to understand the purpose/mission of the project | 15% |
| Prior experience with similar projects | 10% |
| Overall project approach | 20% |
| Favorable past experiences of the school and/or references in working with the vendor | 20% |

Total										100%

Evaluation of the proposals is expected to be completed within ten (10) calendar days after the stated closing date.  The school's project team will evaluate proposals on a variety of quantitative and qualitative criteria.  The proposal selected shall be the proposal deemed to be in the best interests of the District while providing the most cost-effective approach to meet the stated requirements.  The lowest priced proposal will not necessarily be selected.

The District reserves the right to a) reject any or all proposals, or to make no award, b) require modifications to initial proposals or c) to make partial or multiple awards.  The District reserves the right to request clarification or explanation on any proposal submitted.  The District further reserves the right to excuse technical defects in a proposal when, in its sole discretion, such excuse is in the best interests of the District.

11.  	SELECTION SCHEDULE

NAME										DATE

| Request for Proposals Released | March 4, 2015 |
| --- | --- |
| Pre-Bid Meeting | March 19, 2015 – 9:00 AM |
| Final day for question submittal | April 6, 2015 |
| Receive Proposals To Be Received by 10:00 AM local time | April 9, 2015 |
| Vendor Proposals open @ 12:00 PM local time | April 9, 2015 |

APPENDIX A

BID PROPOSAL

Hazlehurst School District Bid Proposal

Football Stadium Lighting Project

Hazlehurst, MS

The undersigned bidder, in compliance with your request for bids for the lighting equipment at the above project, having examined specifications, related documents, and site of the proposed project, hereby proposes to furnish the lighting equipment material as described in the specifications. These prices are for all labor and materials and are to cover the specified equipment and delivery charges.  The contract for bid item “A” will be based on the bid item “C” (The total cost of bid item A and bid item B).

# A.  Bid Price:							$_________________

(Initial System Purchase Price)

# B.  25-Year Operating Cost:					$_________________

(From Section 1.4, Item H – Life-cycle Cost)	(For Evaluation Only)

# C.  Total Cost of Ownership after 25 Years:			$_________________

(Add item “A” and “B”) 	(For Evaluation Only)

________________________________________________________________

Company Name

Authorized Signature

Address

City/State/ZIP

Telephone

Date